## TFR
| Base | 100 | MVA |  |  | 220 | kV |  |  | 220 | 132 |  | 132
| Source -1 |  |  | Line |  |  |  |  | ICT/TFR |  |  |  | Source-2
| Source MVA |  | Source pu imp | Line imp per km | km | line kV | Line pu imp |  | ICT/TFR MVA |  | % Imp | Imp pu | Source MVA | Source pu imp
3 Ph | 10258 | X1 | 0.0097485 | 0.4 | 100 | 220 | 0.082645 |  | 50 | HV-MV | 15% | 0.3 | 5000 | 0.02
1 Ph | 12025 | Xo | 0.005451 | 1.264 | 100 | 220 | 0.26116 | [5 empty] | 4000 | 0.035
[5 empty] | Base Curr | 262.4396 |  | F |  |  | MV base curr | 437.3994
| Pos seq |  | 0.092393 | [5 empty] | 0.32
| Curr dist factors |  | 0.77596 | [5 empty] | 0.22404
| Zero seq |  | 0.26661 | [5 empty] | 0.335
| Curr dist factors |  | 0.55684 | [5 empty] | 0.44316
| Pos seq |  |  |  | 0.071693
| Zero seq |  |  |  | 0.14846
| Total imp |  |  |  | 0.29184
| I1=I2=Io |  |  |  | 3.4265 |  | Amp |  | MVA
| 3Io |  |  |  | 10.2794 |  | 2697.7319 |  | 783.4213
|  |  | pu | [5 empty] | HV
| Current Dist | I1 | 2.6588 | [5 empty] | 0.76767
|  | I2 | 2.6588 | [5 empty] | 0.76767
|  | Io | 1.908 | [5 empty] | 1.5185
|  | Ia | 7.2256 | [5 empty] | 3.0538
|  | Ib | -0.7508 | [5 empty] | 0.7508
|  | Ic | -0.7508 | [5 empty] | 0.7508
|  |  | Amp | [5 empty] | Amp
|  | Ia | 1896.2881 | [5 empty] | 801.4438
|  | Ib | -197.0403 | [5 empty] | 197.0403
|  | Ic | -197.0403 | [5 empty] | 197.0403
|  | Current in fault |  | 2697.7319

## ICT with Tertiary
| Base | 100 | MVA |  |  | 220 | kV |  |  | 220 | 110 | 33 | kV |  | 110
| Source -1 |  |  | Line |  |  |  |  | ICT/TFR | [5 empty] | Source-2
| Source MVA |  | Source pu imp | Line imp per km | km | line kV | Line pu imp |  | ICT/TFR MVA |  | % Imp | Imp pu | Star |  | Source MVA | Source pu imp
3 Ph | 10258 | X1 | 0.0097485 | 0.4 | 50 | 220 | 0.041322 |  | 200 | HV-MV | 15% | 0.075 | 0.0625 | HV | 5000 | 0.02
1 Ph | 12025 | Xo | 0.005451 | 1.264 | 50 | 220 | 0.13058 |  | 200 | HV-LV | 35% | 0.175 | 0.0125 | LV | 5500 | 0.014545
[9 empty] | 200 | MV-LV | 25% | 0.125 | 0.1125 | T
[5 empty] | Base Curr | 262.4396 |  |  |  |  | MV base curr | 524.8793
|  | Source-1 |  | Line | [6 empty] | ICT | [5 empty] | Source-2
Fault
AT Check
|  | 3728.8148 |  | 1.8182 |  | 6645.3142 |  |  | 2916.4994 |  |  | 2651.4505 | IV |  | 5302.901
|  |  |  | A ph curr ratio | [5 empty] | 1020.2036 |  | 265.0489 | Tertiary
[12 empty] | 2916.4994 | Total
|  |  | -593.0951 |  |  |  |  | 593.0951 |  |  | 593.0951 |  | 656.0924 |  |  | 656.0924
| -593.0951 | 2542.6246 | [7 empty] | 4102.6896
6615.0858
[5 empty] | 2542.6246 |  | 4102.6896
| Pos seq |  | 0.051071 | [5 empty] | 0.095
| Curr dist factors |  | 0.65037 | [5 empty] | 0.34963 |  |  | MV+T+S-2 | S-2 + MV
| Zero seq |  | 0.13603 | [5 empty] | 0.084304 |  |  | 0.021804 | 0.027045
| Curr dist factors |  | 0.38262 | [5 empty] | 0.61738 |  |  | 0.19381 |  |  | 0.80619
| Pos seq |  |  |  | 0.033215 | [6 empty] | (T) |  |  | (MV)
| Zero seq |  |  |  | 0.052048
| Total imp |  |  |  | 0.11848
| I1=I2=Io |  |  |  | 8.4404 |  | Amp |  | MVA
| 3Io |  |  |  | 25.3213 |  | 6645.3142 |  | 1929.7992
|  |  | pu | [5 empty] | HV |  |  | MV | Tertiary |  | Source-2
| Current Dist | I1 | 5.4894 | [5 empty] | 2.951 |  |  | 2.951 | 0 |  | 2.951
|  | I2 | 5.4894 | [5 empty] | 2.951 |  |  | 2.951 | 0 |  | 2.951
|  | Io | 3.2295 | [5 empty] | 5.211 |  |  | 4.201 | 1.0099 |  | 4.201
|  | Ia | 14.2083 | [5 empty] | 11.113 |  |  | 10.1031 | 1.0099 |  | 10.1031
|  | Ib | -2.2599 | [5 empty] | 2.2599 |  |  | 1.25 | 1.0099 |  | 1.25
|  | Ic | -2.2599 | [5 empty] | 2.2599 |  |  | 1.25 | 1.0099 |  | 1.25
|  |  | Amp | [5 empty] | Amp |  | LV/HV
|  | Ia | 3728.8148 | [5 empty] | 2916.4994 |  | 1.8182 | 5302.901 | 1020.2036 |  | 5302.901
|  | Ib | -593.0951 | [5 empty] | 593.0951 |  | 1.1062 | 656.0924 | 1020.2036 |  | 656.0924
|  | Ic | -593.0951 | [5 empty] | 593.0951 |  | 1.1062 | 656.0924 | 1020.2036 |  | 656.0924
|  | Current in fault |  | 6645.3142 | Amp
[14 empty] | kV | Deg
|  | Voltages | At Fault | V1 | 0.71965 |  |  |  |  | 0 | j |  |  | 0 | 0
|  |  |  | V2 | -0.28035 | (-0.5-j0.866)*V1+(-0.5+j0.866)*V2+V0 |  |  |  | -0.65896 | -0.866 | 1.0882 | 0.92034 | 138.224 | 52.7318
|  |  |  | V0 | -0.4393 | (-0.5+j0.866)*V1+(-0.5-j0.866)*V2+V0 |  |  |  | -0.65896 | 0.866 | 1.0882 | -0.92034 | 138.224 | -52.7318
| At Vs | V1 | 0.94649 | [5 empty] | Va | 0.87537 |  | 0.87537 |  | 111.1901
|  | V2 | -0.053513 | [5 empty] | Vb | -0.46409 | -0.866 | 0.98252 | 1.0788 | 124.7999 | 61.8131
|  | V0 | -0.017604 | [5 empty] | Vc | -0.46409 | 0.866 | 0.98252 | -1.0788 | 124.7999 | -61.8131
| Zero seq Factor | Kn | 0.72
|  | Zline | Vrn/(Ia+Kn*In) | 20 | OK | As measured by dist relay at S-1

## LV fault
Base | 100 | MVA | 220 | kV |  |  |  |  | 22 | kV | 3 | kV
| Source -1 | [7 empty] | TFR
| Source MVA |  | Source pu imp | [5 empty] | ICT/TFR MVA |  | % Imp | Imp pu | Star
3 Ph | 9868.936 | X1 | 0.010133 | [5 empty] | 50 | HV-LV | 15% | 0.3 | 0.2 | H
1 Ph | 11050.16 | Xo | 0.0068833 | [5 empty] | 50 | HV-T | 30% | 0.6 | 0.1 | L
|  | Base Curr | 262.4396 | [5 empty] | 50 | LV-T | 25% | 0.5 | 0.4 | T
[11 empty] | LV base curr | 2624.3964
AT Check
[6 empty] | 412.135 | IV
|  | 365.3034 |  |  |  | 0.21287 | Tertiary
[5 empty] | 9.013 | 412.3478 | Total |  | 4121.3495 |  |  | 4121.3495 |  |  | 11.282
|  | -46.8315 | [7 empty] | 0
[5 empty] | -46.8315 |  | 0
[9 empty] | 1.7 | Ohm
|  |  | 271.6403 | [5 empty] | NGR
| Pos seq |  | 0.31013 |  |  | HV | Tertiary | LV
| Curr dist factors |  | 1 |  |  | 1 | 0 | 1 | LV + NGR | NGR | S+H II T | S+H
| Zero seq |  | 1.2901 | [5 empty] | 1.1537 | 0.35124 | 0.13636 | 0.20688
| Curr dist factors |  |  |  |  | 0.65911 | 0.34089 | 1
| Pos seq |  |  |  |  | 0.31013
| Zero seq |  |  |  |  | 1.2901
| Total imp |  |  |  |  | 1.9103
LV
| I1=I2=Io |  |  |  |  | 0.52347 |  | Amp
| 3Io |  |  |  |  | 1.5704 |  | 4121.3495
[6 empty] | HV | Ter | pu
| pu Curr | I1 |  |  |  | 0.52347 | 0 | 0.52347
|  | I2 |  |  |  | 0.52347 | 0 | 0.52347
|  | Io |  |  |  | 0.34502 | 0.17845 | 0.52347
|  | Ia |  |  |  | 1.392 | 0.17845 | 1.5704
|  | Ib |  |  |  | -0.17845 | 0.17845 | 0
|  | Ic |  |  |  | -0.17845 | 0.17845 | 0
|  | Ia |  |  |  | 365.3034 | 9.013 | 4121.3495
|  | Ib |  |  |  | -46.8315 | 9.013 | 0
|  | Ic |  |  |  | -46.8315 | 9.013 | 0
|  | V1 | 0.83766
|  | V2 | -0.16234
|  | V0 | -0.67531
[10 empty] | j |  |  | kV |  | Deg
|  | Va | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 |  | 0
|  | Vb | a2V1+aV2+V0 |  | (-0.5-j0.866)*E53+(-0.5+j0.866)*E54+V0 |  |  |  | -1.013 | -0.866 | 1.3327 | 0.70734 | 16.9279 |  | 40.5276
|  | Vc | aV1+a2V2+V0 |  | (-0.5+j0.866)*E53+(-0.5-j0.866)*E54+V0 |  |  |  | -1.013 | 0.866 | 1.3327 | -0.70734 | 16.9279 |  | -40.5276

## Notes
TFR LV side faults
Due to the tertiary or due to the tank 'phantom tertiary' effect, the zero sequence current on the primary side does not maintain the TFR ratio with the zero sequence current
on the secondary side. The total ATs on HV shall be equal to the Secondary ATs plus tertiary ATs.
Although I1 and I2 are in the TFR ratio (Io is not as per TFR ratio), due to the above, the phase currents shall not be in the TFR ratio.
This may cause mal-operation of the TFR diff relay on through faults. Hence Io removal reqd.
Grid faults
The zero sequence currents do no maintain their ratio due to the presence of the tertiary or the tank phantom effect.
This can cause mal-operation of the diff relay.
Single phase units:
If the tertiary is not used, and if there is a source on LV side too, I1, I2 and Io are transferred bet HV and LV.
Phase currents maintain their ratio.
However, presence of the tertiary helps reduce voltages in un-faulted phases. But then Io does not maintain the ration bet HV and MV. Hence removal of Io is required.

## Sheet2
315 | MVA | 400 | 220 | 33
|  | 454.7 | 826.7 | 1837
LV_HV | 166.87 | 415.15 |  | 1.4364 | 10.3719 | 13.85%
LV-IV | 258.13 | 415.25 |  | 0.9288 | 10.3719 | 8.955%
Zero Seq Imp
HV-IV | 52.573 |  |  |  |  | 13.14% | 400 | 8.8 | 22 | 507.9365 | 12.99%
HV-LV | 128 | 44.9 |  | 202.5296 | 507.9365 | 39.87% | 153 | 9.98 | 65.2288 | 507.9365 | 38.53%
IV-LV | 245 | 17.2 |  | 40.5335 | 153.648 | 26.38% | 295 | 3.9 | 13.2203 | 153.6508 | 25.81%